Water & Wastewater Infrastructure Services

439 McFarlan Road

Kennett Square, PA 19348

Phone: 610-444-3551

Fax: 610-444-8132

December 2024

Attention: Ms. Kelly Verna

935 N. Providence Road

Media, PA. 19063

RE: Sanitary Sewer Operations Maintenance Supervisors Report- December- 2024

- Operational Status of the facilities & General Pump Station Status

KBX performed the following general pump station repairs and observations:

December- 2024-general pump station repairs:

General Collections:

Bortondale:

- 12/3/24-Responded to a high water and back up float system active alarms. Upon arrival, contractors were on site doing demolition work on the old station.

- 12/3/24-Responded to high water/back up float alarm. Contractors were the cause of alarms.

- 12/19/24-Met with contractor for Soft Start installation.

Braves Trail:

- Routine Maintenance

Letitia Lane Pump Station:

- Routine Maintenance

Media Station:

- Routine Maintenance

Rose Tree Lower

- 12/31/24-Troubleshot pump #1. Found a broken auxiliary, although still working will need to be replaced.

Rose Tree Park

- 12/5/24- Filled generator with fuel

Rose Tree Upper

- Routine Maintenance

Toft Woods:

- Routine Maintenance

Valley View:

- 12/15/24-Responded to a lag alarm. Cleaned solenoid #2. Observed proper operation before departure.

Winter Street:

- 12/3/24- Responded to lag alarms. Upon arrival pump #2 was shorted to ground. Put pump#1 in lead.

- 12/15/24-Responded to high water alarm. Upon arrival, pump #1 had tripped at thermal. Call in vacuum truck. Cleaned contacts and reset thermal. Observed proper operation before departure.

- 12/15/24-Emergency call out for highwater alarm.

- 12/19/24-Pulled pump #2 to retrieve tag information.

Recommendations for Repairs**

***Please inform us which repairs are the responsibility of the contractor who did the station build outs and upgrades and which you would like us to attend to/fix.

Please let us know if you have any questions or concerns.

KBX Golden, LLC

439 McFarlan Road

Kennett Square, Pa.